## Homing 3
| Home switch | Positive switch | Negative switch | Zero pulse | Motor effects
Input | I1 (set via hm08) | I2 (set via hm07) | I3 (set via hm06)
Case 1:
Starting position | Low | inactive | inactive | inactive | Motor is spinning CW at hm02 speed
Step 1: | goes High | inactive | inactive | inactive | Motor starts spinning CCW at hm03 speed
Step 2: | goes Low | inactive | inactive | inactive | Motor continues spinning CCW at hm03 speed; system looking for zero pulse signal
Step 3: | Low | inactive | inactive | goes High | Motor stops spinning; target reached
Case 2:
Starting position | High | inactive | inactive | inactive | Motor is spinning CCW at hm03 speed
Step 1: | goes Low | inactive | inactive | inactive | Motor continues spinning CCW at hm03 speed; system looking for zero pulse signal
Step 2: | Low | inactive | inactive | goes High | Motor stops spinning; target reached

## Homing 4
| Home switch | Positive switch | Negative switch | Zero pulse | Motor effects
Input | I1 (set via hm08) | I2 (set via hm07) | I3 (set via hm06)
Case 1:
Starting position | Low | inactive | inactive | inactive | Motor is spinning CW at hm03 speed
Step 1: | goes High | inactive | inactive | inactive | Motor continues to spin CW at hm03 speed; system looking for zero pulse signal
Step 2: | High | inactive | inactive | goes High | Motor stops spinning; target reached
Case 2:
Starting position | High | inactive | inactive | inactive | Motor is spinning CCW at hm02 speed
Step 1: | Goes Low | inactive | inactive | inactive | Motor starts spinning CW at hm03 speed
Step 2: | Goes High | inactive | inactive | inactive | Motor continues to spin CW at hm03 speed; system looking for zero pulse signal
Step 3: | High | inactive | inactive | goes High | Motor stops spinning; target reached

## Homing 5
| Home switch | Positive switch | Negative switch | zero pulse | Motor effects
Input | I1 (set via hm08) | I2 (set via hm07) | I3 (set via hm06)
Case 1:
Starting position | Low | inactive | inactive | inactive | Motor is spinning CCW at hm02 speed
Step 1: | Goes High | inactive | inactive | inactive | Motor starts spinning CW at hm03 speed
Step 2: | Goes Low | inactive | inactive | inactive | Motor continues spinning CW at hm03 speed; system looking for zero pulse signal
Step 3: | Low | inactive | inactive | goes High | Motor stops spinning; target reached
Case 2:
Starting position | High | inactive | inactive | inactive | Motor is spinning CW at hm03 speed
Step 1: | Goes Low | inactive | inactive | inactive | Motor continues spinning CW at hm03 speed; system looking for zero pulse signal
Step 2: | Low | inactive | inactive | goes High | Motor stops spinning; target reached

## Homing 6
| Home switch | Positive switch | Negative switch | zero pulse | Motor effects
Input | I1 (set via hm08) | I2 (set via hm07) | I3 (set via hm06)
Case 1:
Starting position | Low | inactive | inactive | inactive | Motor is spinning CCW at hm03 speed
Step 1: | goes High | inactive | inactive | inactive | Motor conitnues to spin CCW at hm03 speed; system looking for zero pulse signal
Step 2: | High | inactive | inactive | goes High | Motor stops spinning; target reached
Case 2:
Starting position | High | inactive | inactive | inactive | Motor is spinning CW at hm02 speed
Step 1: | goes Low | inactive | inactive | inactive | Motor starts spinning CCW at hm03 speed
Step 2: | goes High | inactive | inactive | inactive | Motor conitnues to spin CCW at hm03 speed; system looking for zero pulse signal
Step 3: | High | inactive | inactive | goes High | Motor stops spinning; target reached

## Homing 7
| Home switch | Positive switch | Negative switch | zero pulse | Motor effects
Input | I1 (set via hm08) | I2 (set via hm07) | I3 (set via hm06)
Case 1:
Starting position | Low | High | inactive | inactive | Motor is spinning CW at hm02 speed
Step 1: | Low | goes Low | inactive | inactive | Motor starts spinning CCW at hm02 speed
Step 2: | Low | goes High | inactive | inactive | Motor continues to spin CCW at hm02 speed
Step 3: | goes High | High | inactive | inactive | Motor starts spinning CCW at hm03 speed
Step 4: | goes Low | High | inactive | inactive | Motor continues to spin CCW at hm03 speed; system looking for zero pulse signal
Step 5: | Low | High | inactive | goes High | Motor stops spinning; target reached
Case 2:
Starting position | Low | High | inactive | inactive | Motor is spinning CW at hm02 speed
Step 1: | Goes High | High | inactive | inactive | Motor starts spinning CCW at hm03 speed
Step 2: | Goes Low | High | inactive | inactive | Motor continues to spin CCW at hm03 speed; system looking for zero pulse signal
Step 3: | Low | High | inactive | goes High | Motor stops spinning; target reached
Case 3:
Starting position | High | High | inactive | inactive | Motor starts spinning CCW at hm03 speed
Step 1: | Goes Low | High | inactive | inactive | Motor continues to spin CCW at hm03 speed; system looking for zero pulse signal
Step 2: | Low | High | inactive | goes High | Motor stops spinning; target reached

## Homing 8
| Home switch | Positive switch | Negative switch | zero pulse | Motor effects
Input | I1 (set via hm08) | I2 (set via hm07) | I3 (set via hm06)
Case 1:
Starting position | Low | High | inactive | inactive | Motor is spinning CW at hm03 speed
Step 1: | Low | goes Low | inactive | inactive | Motor starts spinning CCW at hm02 speed
Step 2: | Low | goes High | inactive | inactive | Motor continues to spin CCW at hm02 speed
Step 3: | goes High | High | inactive | inactive | Motor continues to spin CCW at hm02 speed
Step 4: | Goes Low | High | inactive | inactive | Motor starts spinning CW at hm03 speed
Step 5: | Goes High | High | inactive | inactive | Motor continues to spin CW at hm03 speed; system looking for zero pulse signal
Step 6: | High | High | inactive | goes High | Motor stops spinning; target reached
Case 2:
Starting position | Low | High | inactive | inactive | Motor is spinning CW at hm03 speed
Step 1: | Goes High | High | inactive | inactive | Motor continues to spin CW at hm03 speed; system looking for zero pulse signal
Step 2: | High | High | inactive | goes High | Motor stops spinning; target reached
Case 3:
Starting position | High | Low | inactive | inactive | Motor is spinning CCW at hm02 speed
Step 1: | HIgh | goes High | inactive | inactive | Motor continues to spin CCW at hm02 speed
Step 2: | Goes Low | High | inactive | inactive | Motor starts spinning CW at hm03 speed
Step 3: | Goes High | High | inactive | inactive | Motor continues to spin CW at hm03 speed; system looking for zero pulse signal
Step 4: | High | High | inactive | goes High | Motor stops spinning; target reached

## Homing 9
| Home switch | Positive switch | Negative switch | zero pulse | Motor effects
Input | I1 (set via hm08) | I2 (set via hm07) | I3 (set via hm06)
Case 1:
Starting position | Low | High | inactive | inactive | Motor is spinning CW at hm02 speed
Step 1: | Low | Goes Low | inactive | inactive | Motor starts spinning CCW at hm03 speed
Step 2: | Low | Goes HIgh | inactive | inactive | Motor continues to spin CCW at hm03 speed
Step 3: | Goes High | High | inactive | inactive | Motor contines to spin CCW at hm03 speed; system looking for zero pulse signal
Step 4: | High | High | inactive | goes High | Motor stops spinning; target reached
Case 2:
Starting position | Low | High | inactive | inactive | Motor is spinning CW at hm02 speed
Step 1: | Goes High | High | inactive | inactive | Motor continues to spin CW at hm02 speed
Step 2: | Goes Low | High | inactive | inactive | Motor continues to spin CCW at hm03 speed
Step 3: | Goes High | High | inactive | inactive | Motor contines to spin CCW at hm03 speed; system looking for zero pulse signal
Step 4: | High | High | inactive | goes High | Motor stops spinning; target reached
Case 3:
Starting position | High | High | inactive | inactive | Motor is spinning CW at hm02 speed
Step 1: | Goes Low | High | inactive | inactive | Motor continues to spin CCW at hm03 speed
Step 2: | Goes High | High | inactive | inactive | Motor contines to spin CCW at hm03 speed; system looking for zero pulse signal
Step 3: | High | High | inactive | goes High | Motor stops spinning; target reached

## Homing 10
| Home switch | Positive switch | Negative switch | zero pulse | Motor effects
Input | I1 (set via hm08) | I2 (set via hm07) | I3 (set via hm06)
Case 1:
Starting position | Low | High | inactive | inactive | Motor is spinning CW at hm02 speed
Step 1: | Low | goes Low | inactive | inactive | Motor starts spinning CCW at hm02 speed
Step 2: | Low | goes High | inactive | inactive | Motor continues to spin CCW at hm02 speed
Step 3: | goes High | High | inactive | inactive | Motor starts spinning CW at hm03 speed
Step 4: | goes Low | High | inactive | inactive | Motor continues to spin CW at hm03; system looking for zero pulse signal
Step 5: | Low | High | inactive | goes High | Motor stops spinning; target reached
Case 2:
Starting position | Low | High | inactive | inactive | Motor is spinning CW at hm02 speed
Step 1: | goes High | High | inactive | inactive | Motor starts spinning CW at hm03 speed
Step 2: | goes Low | High | inactive | inactive | Motor continues to spin CW at hm03; system looking for zero pulse signal
Step 3: | Low | High | inactive | goes High | Motor stops spinning; target reached
Case 3:
Starting position | High | High | inactive | inactive | Motor is spinning CW at hm03 speed
Step 1: | goes Low | High | inactive | inactive | Motor continues to spin CW at hm03; system looking for zero pulse signal
Step 2: | Low | High | inactive | goes High | Motor stops spinning; target reached

## Homing 11
| Home switch | Positive switch | Negative switch | zero pulse | Motor effects
Input | I1 (set via hm08) | I2 (set via hm07) | I3 (set via hm06)
Case 1:
Starting position | Low | inactive | High | inactive | Motor is spinning CCW at hm02 speed
Step 1: | Low | inactive | goes Low | inactive | Motor starts spinning CW at hm02 speed
Step 2: | Low | inactive | goes High | inactive | Motor continues to spin CW at hm02 speed
Step 3: | goes High | inactive | High | inactive | Motor starts spinning CW at hm03 speed
Step 4: | goes Low | inactive | High | inactive | Motor continues to spin CW at hm03 speed; system looking for zero pulse signal
Step 5: | Low | inactive | High | goes High | Motor stops spinning; target reached
Case 2:
Starting position | Low | inactive | High | inactive | Motor is spinning CCW at hm02 speed
Step 1: | goes High | inactive | High | inactive | Motor starts spinning CW at hm03 speed
Step 2: | goes Low | inactive | High | inactive | Motor continues to spin CW at hm03 speed; system looking for zero pulse signal
Step 3: | Low | inactive | High | goes High | Motor stops spinning; target reached
Case 3:
Starting position | High | inactive | High | inactive | Motor is spinning CW at hm03 speed
Step 1: | goes Low | inactive | High | inactive | Motor continues to spin CW at hm03 speed; system looking for zero pulse signal
Step 2: | Low | inactive | High | goes High | Motor stops spinning; target reached

## Homing 12
| Home switch | Positive switch | Negative switch | zero pulse | Motor effects
Input | I1 (set via hm08) | I2 (set via hm07) | I3 (set via hm06)
Case 1:
Starting position | Low | inactive | High | inactive | Motor is spinning CCW at hm02 speed
Step 1: | Low | inactive | goes Low | inactive | Motor starts spinning CW at hm02 speed
Step 2: | Low | inactive | goes High | inactive | Motor continues to spin CW at hm02 speed
Step 3: | goes High | inactive | High | inactive | Motor continues to spin CW at hm02 speed
Step 4: | goes Low | inactive | High | inactive | Motor starts spinning CCW at hm03 speed
Step 5: | goes High | inactive | High | inactive | Motor continues to spin CCW at hm03 speed; system looking for zero pulse signal
Step 6: | High | inactive | High | goes High | Motor stops spinning; target reached
Case 2:
Starting position | Low | inactive | High | inactive | Motor is spinning CCW at hm03 speed
Step 1: | goes High | inactive | High | inactive | Motor continues to spin CCW at hm03 speed; system looking for zero pulse signal
Step 2: | High | inactive | High | goes High | Motor stops spinning; target reached
Case 3:
Starting position | High | inactive | High | inactive | Motor is spinning CW at hm02 speed
Step 1: | goes Low | inactive | High | inactive | Motor starts spinning CCW at hm03 speed
Step 2: | goes High | inactive | High | inactive | Motor continues to spin CCW at hm03 speed; system looking for zero pulse signal
Step 3: | High | inactive | High | goes High | Motor stops spinning; target reached

## Homing 13
| Home switch | Positive switch | Negative switch | zero pulse | Motor effects
Input | I1 (set via hm08) | I2 (set via hm07) | I3 (set via hm06)
Case 1:
Starting position | Low | inactive | High | inactive | Motor is spinning CCW at hm02 speed
Step 1: | Low | inactive | goes Low | inactive | Motor starts spinning CW at hm03 speed
Step 2: | Low | inactive | goes High | inactive | Motor starts spinning CW at hm03 speed
Step 3: | goes High | inactive | High | inactive | Motor continues to spin CW at hm03 speed; system looking for zero pulse signal
Step 4: | High | inactive | High | goes High | Motor stops spinning; target reached
Case 2:
Starting position | Low | inactive | High | inactive | Motor is spinning CCW at hm02 speed
Step 1: | goes High | inactive | High | inactive | Motor continues to spin CCW at hm02 speed
Step 2: | goes Low | inactive | High | inactive | Motor starts spinning CW at hm03 speed
Step 3: | goes High | inactive | High | inactive | Motor continues to spin CW at hm03 speed; system looking for zero pulse signal
Step 4: | High | inactive | High | goes High | Motor stops spinning; target reached
Case 3:
Starting position | High | inactive | High | inactive | Motor is spinning CCW at hm02 speed
Step 1: | goes Low | inactive | High | inactive | Motor starts spinning CW at hm03 speed
Step 2: | goes High | inactive | High | inactive | Motor continues to spin CW at hm03 speed; system looking for zero pulse signal
Step 3: | High | inactive | High | goes High | Motor stops spinning; target reached

## Homing 14
| Home switch | Positive switch | Negative switch | zero pulse | Motor effects
Input | I1 (set via hm08) | I2 (set via hm07) | I3 (set via hm06)
Case 1:
Starting position | Low | inactive | High | inactive | Motor is spinning CCW at hm02 speed
Step 1: | Low | inactive | goes Low | inactive | Motor starts spinning CW at hm02 speed
Step 2: | Low | inactive | goes High | inactive | Motor continues to spin CW at hm02 speed
Step 3: | goes High | inactive | High | inactive | Motor starts to spin CCW at hm03 speed
Step 4: | goes Low | inactive | High | inactive | Motor continues to spin CCW at hm03 speed; system looking for zero pulse signal
Step 5: | Low | inactive | High | goes High | Motor stops spinning; target reached
Case 2:
Starting position | Low | inactive | High | inactive | Motor is spinning CCW at hm02 speed
Step 1: | goes High | inactive | High | inactive | Motor starts spinning CCW at hm03 speed
Step 2: | goes Low | inactive | High | inactive | Motor continues to spin CCW at hm03 speed; system looking for zero pulse signal
Step 3: | Low | inactive | High | goes High | Motor stops spinning; target reached
Case 3:
Starting position | High | inactive | High | inactive | Motor is spinning CCW at hm03 speed
Step 1: | goes Low | inactive | High | inactive | Motor continues to spin CCW at hm03 speed; system looking for zero pulse signal
Step 2: | High | inactive | High | goes High | Motor stops spinning; target reached

## Homing 17
| Home switch | Positive switch | Negative switch | Motor effects
Input | I1 (set via hm08) | I2 (set via hm07) | I3 (set via hm06)
Case 1:
Starting position | Inactive | Inactive | High | Motor is spinning CCW at hm02 speed
Step 1: | Inactive | Inactive | Low | Motor starts spinning CW at hm03 speed

## Homing 18
| Home switch | Positive switch | Negative switch | Motor effects
Input | I1 (set via hm08) | I2 (set via hm07) | I3 (set via hm06)
Case 1:
Starting position | Inactive | High | Inactive | Motor is spinning CW at hm02 speed
Step 1: | Inactive | goes Low | Inactive | Motor starts to spin CCW at hm03 speed

## Homing 19
| Home switch | Positive switch | Negative switch | Motor effects
Input | I1 (set via hm08) | I2 (set via hm07) | I3 (set via hm06)
Case 1:
Starting position | Low | inactive | inactive | Motor is spinning CW at hm02 speed
Step 1: | goes High | inactive | inactive | Motor starts spinning CCW at hm03 speed
Step 2: | goes Low | inactive | inactive | Motor stops spinning; target reached
Case 2:
Starting position | High | inactive | inactive | Motor is spinning CCW at hm03 speed
Step 1: | goes Low | inactive | inactive | Motor stops spinning; target reached

## Homing 20
| Home switch | Positive switch | Negative switch | Motor effects
Input | I1 (set via hm08) | I2 (set via hm07) | I3 (set via hm06)
Case 1:
Starting position | Low | inactive | inactive | Motor is spinning CW at hm03 speed
Step 1: | goes High | inactive | inactive | Motor stops spinning; target reached
Case 2:
Starting position | High | inactive | inactive | Motor is spinning CCW at hm02 speed
Step 1: | Goes Low | inactive | inactive | Motor starts spinning CW at hm03 speed
Step 2: | Goes High | inactive | inactive | Motor stops spinning; target reached

## Homing 21
| Home switch | Positive switch | Negative switch | Motor effects
Input | I1 (set via hm08) | I2 (set via hm07) | I3 (set via hm06)
Case 1:
Starting position | Low | inactive | inactive | Motor is spinning CCW at hm02 speed
Step 1: | Goes High | inactive | inactive | Motor starts spinning CW at hm03 speed
Step 2: | Goes Low | inactive | inactive | Motor stops spinning; target reached
Case 2:
Starting position | High | inactive | inactive | Motor is spinning CW at hm03 speed
Step 1: | Goes Low | inactive | inactive | Motor stops spinning; target reached

## Homing 22
| Home switch | Positive switch | Negative switch | Motor effects
Input | I1 (set via hm08) | I2 (set via hm07) | I3 (set via hm06)
Case 1:
Starting position | Low | inactive | inactive | Motor is spinning CCW at hm03 speed
Step 1: | goes High | inactive | inactive | Motor stops spinning; target reached
Case 2:
Starting position | High | inactive | inactive | Motor is spinning CW at hm02 speed
Step 1: | goes Low | inactive | inactive | Motor starts spinning CCW at hm03 speed
Step 2: | goes High | inactive | inactive | Motor stops spinning; target reached

## Homing 23
| Home switch | Positive switch | Negative switch | Motor effects
Input | I1 (set via hm08) | I2 (set via hm07) | I3 (set via hm06)
Case 1:
Starting position | Low | High | inactive | Motor is spinning CW at hm02 speed
Step 1: | Low | goes Low | inactive | Motor starts spinning CCW at hm02 speed
Step 2: | Low | goes High | inactive | Motor continues to spin CCW at hm02 speed
Step 3: | goes High | High | inactive | Motor starts spinning CCW at hm03 speed
Step 4: | goes Low | High | inactive | Motor stops spinning; target reached
Case 2:
Starting position | Low | High | inactive | Motor is spinning CW at hm02 speed
Step 1: | Goes High | High | inactive | Motor starts spinning CCW at hm03 speed
Step 2: | Goes Low | High | inactive | Motor stops spinning; target reached
Case 3:
Starting position | High | High | inactive | Motor starts spinning CCW at hm03 speed
Step 1: | Goes Low | High | inactive | Motor stops spinning; target reached

## Homing 24
| Home switch | Positive switch | Negative switch | Motor effects
Input | I1 (set via hm08) | I2 (set via hm07) | I3 (set via hm06)
Case 1:
Starting position | Low | High | inactive | Motor is spinning CW at hm03 speed
Step 1: | Low | goes Low | inactive | Motor starts spinning CCW at hm02 speed
Step 2: | Low | goes High | inactive | Motor continues to spin CCW at hm02 speed
Step 3: | goes High | High | inactive | Motor continues to spin CCW at hm02 speed
Step 4: | Goes Low | High | inactive | Motor starts spinning CW at hm03 speed
Step 5: | Goes High | High | inactive | Motor stops spinning; target reached
Case 2:
Starting position | Low | High | inactive | Motor is spinning CW at hm03 speed
Step 1: | Goes High | High | inactive | Motor stops spinning; target reached
Case 3:
Starting position | High | Low | inactive | Motor is spinning CCW at hm02 speed
Step 1: | HIgh | goes High | inactive | Motor continues to spin CCW at hm02 speed
Step 2: | Goes Low | High | inactive | Motor starts spinning CW at hm03 speed
Step 3: | Goes High | High | inactive | Motor stops spinning; target reached

## Homing 25
| Home switch | Positive switch | Negative switch | Motor effects
Input | I1 (set via hm08) | I2 (set via hm07) | I3 (set via hm06)
Case 1:
Starting position | Low | High | inactive | Motor is spinning CW at hm02 speed
Step 1: | Low | Goes Low | inactive | Motor starts spinning CCW at hm03 speed
Step 2: | Low | Goes HIgh | inactive | Motor continues to spin CCW at hm03 speed
Step 3: | High | High | inactive | Motor stops spinning; target reached
Case 2:
Starting position | Low | High | inactive | Motor is spinning CW at hm02 speed
Step 1: | Goes High | High | inactive | Motor continues to spin CW at hm02 speed
Step 2: | Goes Low | High | inactive | Motor continues to spin CCW at hm03 speed
Step 3: | Goes High | High | inactive | Motor stops spinning; target reached
Case 3:
Starting position | High | High | inactive | Motor is spinning CW at hm02 speed
Step 1: | Goes Low | High | inactive | Motor continues to spin CCW at hm03 speed
Step 2: | Goes High | High | inactive | Motor stops spinning; target reached

## Homing 26
| Home switch | Positive switch | Negative switch | Motor effects
Input | I1 (set via hm08) | I2 (set via hm07) | I3 (set via hm06)
Case 1:
Starting position | Low | High | inactive | Motor is spinning CW at hm02 speed
Step 1: | Low | goes Low | inactive | Motor starts spinning CCW at hm02 speed
Step 2: | Low | goes High | inactive | Motor continues to spin CCW at hm02 speed
Step 3: | goes High | High | inactive | Motor starts spinning CW at hm03 speed
Step 4: | goes Low | High | inactive | Motor stops spinning; target reached
Case 2:
Starting position | Low | High | inactive | Motor is spinning CW at hm02 speed
Step 1: | goes High | High | inactive | Motor starts spinning CW at hm03 speed
Step 2: | goes Low | High | inactive | Motor stops spinning; target reached
Case 3:
Starting position | High | High | inactive | Motor is spinning CW at hm03 speed
Step 1: | goes Low | High | inactive | Motor stops spinning; target reached

## Homing 27
| Home switch | Positive switch | Negative switch | Motor effects
Input | I1 (set via hm08) | I2 (set via hm07) | I3 (set via hm06)
Case 1:
Starting position | Low | inactive | High | Motor is spinning CCW at hm02 speed
Step 1: | Low | inactive | goes Low | Motor starts spinning CW at hm02 speed
Step 2: | Low | inactive | goes High | Motor continues to spin CW at hm02 speed
Step 3: | goes High | inactive | High | Motor starts spinning CW at hm03 speed
Step 4: | goes Low | inactive | High | Motor stops spinning; target reached
Case 2:
Starting position | Low | inactive | High | Motor is spinning CCW at hm02 speed
Step 1: | goes High | inactive | High | Motor starts spinning CW at hm03 speed
Step 2: | goes Low | inactive | High | Motor stops spinning; target reached
Case 3:
Starting position | High | inactive | High | Motor is spinning CW at hm03 speed
Step 1: | goes Low | inactive | High | Motor stops spinning; target reached

## Homing 28
| Home switch | Positive switch | Negative switch | Motor effects
Input | I1 (set via hm08) | I2 (set via hm07) | I3 (set via hm06)
Case 1:
Starting position | Low | inactive | High | Motor is spinning CCW at hm02 speed
Step 1: | Low | inactive | goes Low | Motor starts spinning CW at hm02 speed
Step 2: | Low | inactive | goes High | Motor continues to spin CW at hm02 speed
Step 3: | goes High | inactive | High | Motor continues to spin CW at hm02 speed
Step 4: | goes Low | inactive | High | Motor starts spinning CCW at hm03 speed
Step 5: | goes High | inactive | High | Motor stops spinning; target reached
Case 2:
Starting position | Low | inactive | High | Motor is spinning CCW at hm03 speed
Step 1: | goes High | inactive | High | Motor stops spinning; target reached
Case 3:
Starting position | High | inactive | High | Motor is spinning CW at hm02 speed
Step 1: | goes Low | inactive | High | Motor starts spinning CCW at hm03 speed
Step 2: | goes High | inactive | High | Motor stops spinning; target reached

## Homing 30
| Home switch | Positive switch | Negative switch | Motor effects
Input | I1 (set via hm08) | I2 (set via hm07) | I3 (set via hm06)
Case 1:
Starting position | Low | inactive | High | Motor is spinning CCW at hm02 speed
Step 1: | Low | inactive | goes Low | Motor starts spinning CW at hm02 speed
Step 2: | Low | inactive | goes High | Motor continues to spin CW at hm02 speed
Step 3: | goes High | inactive | High | Motor starts to spin CCW at hm03 speed
Step 4: | goes Low | inactive | High | Motor stops spinning; target reached
Case 2:
Starting position | Low | inactive | High | Motor is spinning CCW at hm02 speed
Step 1: | goes High | inactive | High | Motor starts spinning CCW at hm03 speed
Step 2: | goes Low | inactive | High | Motor stops spinning; target reached
Case 3:
Starting position | High | inactive | High | Motor is spinning CCW at hm03 speed
Step 1: | goes Low | inactive | High | Motor stops spinning; target reached

## Homing 29
| Home switch | Positive switch | Negative switch | Motor effects
Input | I1 (set via hm08) | I2 (set via hm07) | I3 (set via hm06)
Case 1:
Starting position | Low | inactive | High | Motor is spinning CCW at hm02 speed
Step 1: | Low | inactive | goes Low | Motor starts spinning CW at hm03 speed
Step 2: | Low | inactive | goes High | Motor starts spinning CW at hm03 speed
Step 3: | goes High | inactive | High | Motor stops spinning; target reached
Case 2:
Starting position | Low | inactive | High | Motor is spinning CCW at hm02 speed
Step 1: | goes High | inactive | High | Motor continues to spin CCW at hm02 speed
Step 2: | goes Low | inactive | High | Motor starts spinning CW at hm03 speed
Step 3: | goes High | inactive | High | Motor stops spinning; target reached
Case 3:
Starting position | High | inactive | High | Motor is spinning CCW at hm02 speed
Step 1: | goes Low | inactive | High | Motor starts spinning CW at hm03 speed
Step 2: | goes High | inactive | High | Motor stops spinning; target reached